# T3 Controller SNMP MIB Definition (v5.0)

Project: T3 Programmable Controller on ESP32

Client: PLC Group

Manufacturer: Temco Controls Ltd.

Date: February 2026

## 1. Enterprise Identity & OID Structure

The T3 Controller has migrated from experimental OIDs to the officially assigned IANA Private Enterprise Number (PEN).

- Official IANA PEN: 50523

- Enterprise Root: 1.3.6.1.4.1.50523

- Product Series (T3): 1.3.6.1.4.1.50523.1

- sysObjectID: 1.3.6.1.4.1.50523.1.1

## 2. Updated Output Configuration (PWM Support)

The cfgType mapping (OID column .3) now includes support for Pulse Width Modulation. Hardware Guard: The firmware will validate the physical pin capability before accepting a range change to 14 or 15. If unsupported, the agent returns SNMP_ERR_BADVALUE.

| Value | Range Label | Description | Scaling |
| --- | --- | --- | --- |
| 7 | Binary Output | On/Off Relay or Open Collector | 0 or 1 |
| 8 | Analog Output | 0-10V DC | 0.0 - 10.0 |
| 10 | Analog Output | 0-100% (Standard) | 0.0 - 100.0 |
| 14 | PWM Output | High-Freq Duty Cycle (0-100%) | 0.0 - 100.0 |
| 15 | Freq Counter | High-Speed Pulse Counting | Integer |

## 3. Autonomous Notifications (The "Master Trap")

To eliminate constant polling and simplify NOC (Network Operations Center) integration, the T3 implements a "Master Trap" payload. Every notification is sent as a single v2c Trap containing a bundle of variable bindings (Varbinds).

Trap OID: 1.3.6.1.4.1.50523.1.0.1 (t3AlarmNotification)

### Trap Payload (Varbind List):

- sysLocation (1.3.6.1.2.1.1.6.0): The physical site name (e.g., "Building B, Floor 4").

- eventID (1.3.6.1.4.1.50523.1.4.1): A unique tracking ID to match "Set" and "Clear" events.

- eventSet (1.3.6.1.4.1.50523.1.4.2): 1 = Alarm Active, 0 = Alarm Cleared.

- alarmType (1.3.6.1.4.1.50523.1.4.3): Contextual string (e.g., "AI1 Temperature High").

- alarmValue (1.3.6.1.4.1.50523.1.4.4): The numeric value at the moment of the trigger.

- sysTime (1.3.6.1.2.1.1.3.0): Timestamp of the event.

## 4. Implementation & Memory Optimization

- Virtual Table Mapping: To prevent heap fragmentation and I2C instability, the SNMP agent uses a dynamic OID dispatcher. It does not pre-allocate 1,000 nodes; instead, it parses the Instance ID (1-64) at the time of the request to fetch data from the BACnet tables.

- System Scalability: The number of Inputs, Outputs, and Variables is determined by the T3 logic engine. The SNMP agent dynamically reflects these changes without requiring a firmware re-compile.

## 5. Standard Compliance & Testing

This MIB is designed for compatibility with industry-standard network management tools.

- Required Testing Tools: * iReasoning MIB Browser (Professional): For validating the Varbind bundles and OID paths.

  - Paessler PRTG: For testing NOC-style dashboards and Trap receiver performance.

- Compliance: This implementation follows the SNMP v2c protocol, supporting GetBulk operations for high-efficiency data retrieval.

Notes for developer Fazal:

- Update the .mib source file to replace all TEMCO labels with the numeric ID 50523.

- Implement the hardware capability check in the cfgType write callback.

- Ensure the Trap function uses a single PDU for all Varbinds to meet Tony's "NOC integration" requirement.