GUIDE 1 OF 3

Set up a blank Hub

Bootloader, SoftAP Wi-Fi, T3000, then the first application

Product: Temco Hub

Date: 14 October 2026

A new chip gets the bootloader only. T3000 loads the Hub application after Wi-Fi is set.

# 1. How to read this guide

You type — what you click or enter.

You should see — the screen or the serial text that means the step worked.

If the reply is different, use the troubleshooting table at the end. Do not go on with the wrong COM port or the wrong IP.

The first program on the chip is the bootloader.  The flash tool writes the bootloader. It does not write the Hub application. The bootloader creates the T3_Admin Wi-Fi page, shows the Wi-Fi address and the Modbus ID, and waits for T3000. T3000 is what loads temco_app.bin the first time.

# 2. What you will have when you finish

The bootloader is running. The application slot is still empty.

Your phone can join T3_Admin and open the setup page.

The page shows a normal Wi-Fi address, a Modbus ID, and the baud.

T3000 finds that address.

T3000 has loaded the Hub application. The serial log then says temco_app.

# 3. What you need

## 3.1 On the bench

The Hub, with its normal power supply.

A USB serial cable to the PC. The log is 115200 baud, 8 data bits, no parity, 1 stop bit.

A phone or laptop with Wi-Fi, for the setup page.

A 2.4 GHz Wi-Fi network. The Hub does not join a 5 GHz-only network.

The four bootloader files from the person who built them: bootloader.bin, partition-table.bin, ota_data_initial.bin, and T3_bootloader.bin.

temco_app.bin, kept for T3000. Do not give this file to the flash tool.

## 3.2 Programs to install

| Program | What it is for | Where to get it |
| --- | --- | --- |
| Flash Download Tool, 3.9.2 or newer | Writes the bootloader. The chip button must say ESP32-S3. | https://www.espressif.com/en/support/download/other-tools |
| CH340 driver | Makes the COM port appear, if Windows does not already show one. | https://temcocontrols.com/ftp/file/CH340SerSetup.zip |
| PuTTY | Shows the Hub’s text log. | https://www.chiark.greenend.org.uk/~sgtatham/putty/latest.html |
| T3000 | Finds the Hub and loads the application. | https://assets.temcocontrols.com/products/t3_series_programmable_bacnet__amp_modbus_controller/software_file/09T3000Software-4.zip |

Install each program, then continue. T3000 must be allowed on private networks so it can hear the Hub.

## 3.3 Find the COM port

Install the CH340 driver if Device Manager has no USB serial port.

Plug in the Hub USB cable.

Open Device Manager → Ports (COM & LPT).

You should see

USB-SERIAL CH340 (COM5)

The number may not be COM5. Write down the number you see and use it everywhere this guide says COM5.

Port busy.  If the flash tool or PuTTY says Access is denied, close every other program that uses that COM port. Only one program can have it open.

## 3.4 Open PuTTY

Connection type: Serial.

Serial line: your COM port. Speed: 115200.

Data bits 8, Stop bits 1, Parity None, Flow control None.

Leave PuTTY closed while the flash tool is running. Open it after the flash finishes.

# 4. Put the chip into download mode

Download mode is how the PC is allowed to write the bootloader. Wi-Fi is off in this mode.

Close PuTTY.

Hold the BOOT button.

While BOOT is held, press and release RESET (or EN).

Release BOOT.

If the board has pins instead of buttons, GPIO0 must be held low during the reset pulse, then released.

# 5. Flash the bootloader

Use the Flash Download Tool. Do not add temco_app.bin.

Start the tool. Chip Type: ESP32-S3. WorkMode: Develop. LoadMode: UART.

Fill the rows below and tick each one.

| Tick | File | Address |
| --- | --- | --- |
| Yes | bootloader.bin | 0x0 |
| Yes | partition-table.bin | 0x8000 |
| Yes | ota_data_initial.bin | 0x19000 |
| Yes | T3_bootloader.bin | 0x20000 |

SPI speed 80 MHz. Flash size 32 MB. Use the SPI mode that came with these files. Do not change it to DIO.

COM port: yours. Baud: 460800. If it cannot connect, try 115200.

Put the chip in download mode again, then click START.

You should see

A bar for each file, then FINISH in green.
The log shows Hash of data verified for each file.

A red FAIL means the chip type, the COM port, or an address is wrong. Do not continue.

# 6. Check that the bootloader started

Close the flash tool.

Open PuTTY at 115200.

Press RESET once. Do not hold BOOT.

You should see

bootloader 47, product <n>, count_reboot <n> , baut 9
I (...) WIFI: WiFi station off, Soft AP is up
I (...) WIFI_WEB: SoftAP started. SSID: T3_Admin, Password: T3_Admin, http://tstat.local
I (...) WIFI_WEB: Wi-Fi setup page at http://tstat.local or http://192.168.4.1

47 is the bootloader revision. baut 9 is the baud index. The setup page shows that index as 115200. T3_Admin should appear in the phone’s Wi-Fi list within about 30 seconds.

If the log says temco_app, the application was written too early.  A correct first boot says bootloader 47. Erase the chip and flash again with the four bootloader files only.

# 7. Set the Wi-Fi from the SoftAP page

## 7.1 Join the setup network

| Item | Value |
| --- | --- |
| Wi-Fi name | T3_Admin |
| Password | T3_Admin |
| Page | http://192.168.4.1/ |
| If the name does not open | http://tstat.local/ |

Connected without internet is normal. Stay on T3_Admin. Do not let the phone jump back to the office Wi-Fi.

## 7.2 What the page shows

You type   ·   Phone or PC browser, joined to T3_Admin

http://192.168.4.1/

You should see

Two boxes.

T3 Wi-Fi Setup
  WiFi IP: not connected
  Scan Wi-Fi
  SSID and Password
  Save & Connect

Modbus
  Modbus ID: 1
  Baud: 115200

The page refreshes these lines about every 4 seconds.

Modbus ID 1 is the station number T3000 will use. Baud 115200 is the serial log speed.

## 7.3 Save your Wi-Fi

Click Scan Wi-Fi.

Pick your 2.4 GHz network, or type the name.

Type the password exactly.

Click Save & Connect.

You should see

While scanning: Scanning...
Then: Scan complete

After Save & Connect:
  Saving...
  Saved! Device rebooting...

Serial:
I (...) WIFI_WEB: Wi-Fi credentials saved. SSID: OfficeWiFi. Rebooting...

The password can be up to 31 characters. A longer one is cut off.

## 7.4 Read the address on the same page

Stay on T3_Admin. The bootloader leaves the setup network up so the page can show the new address. Wait 30 to 60 seconds.

You should see

WiFi IP: 192.168.1.50
Modbus ID: 1
Baud: 115200

Serial:
I (...) WIFI: WiFi IP: 192.168.1.50

192.168.1.50 is an example. Use the address on your page.

Write that address down. T3000 uses it, not 192.168.4.1.

Put the PC on the same Wi-Fi the Hub just joined.

Ping that address.

You type   ·   PC on the same Wi-Fi. Use your address.

ping 192.168.1.50

You should see

Reply from 192.168.1.50: bytes=32 time<10ms TTL=64

# 8. Find it in T3000

The PC must be on the same network as the address on the page, not on T3_Admin.

Start T3000 and click the scan icon.

You should see

A new row with that same IP address and Modbus port 502.
This row is still the bootloader. The application is loaded in the next section.

Select the row and connect. The Modbus ID on the page is the station address, usually 1.

# 9. Load the application from T3000

This is the first time temco_app.bin goes into the chip. T3000 sends it. You do not use the flash tool for this file.

In T3000, select the row whose IP matches the SoftAP page.

Menu: Tools → Load firmware for a single device.

Choose temco_app.bin from the Hub build. Do not choose T3_bootloader.bin.

If the window asks for a COM port, that path is for other products. Stay with the network device you already selected.

Start the load. Leave the power on.

You should see

The serial log shows:
I (...) WIFI_WEB: SoftAP stopped for firmware update

T3_Admin drops off while the file is sent. That is expected.
The progress bar finishes.
The Hub reboots.
PuTTY shows:
I (...) app_init: Project name:     temco_app

Scan in T3000 again. The device comes back as the Hub application.

If the bar never moves, ping the address from the page, select that row again, and load temco_app.bin.

If power fails halfway, scan again and start the load once more. T3000 continues from the last good piece. If it reports a bad file, start a fresh load of the same temco_app.bin.

# 10. Pass or fail

| Check | Pass |
| --- | --- |
| Flash tool | FINISH, and Hash of data verified for each file. |
| Serial after reset | bootloader 47, then Soft AP is up. |
| Setup page | WiFi IP: not connected, Modbus ID: 1, Baud: 115200. |
| After Save | The page shows a LAN address. ping of that address works. |
| T3000 | The scan row uses that same address. |
| Application | Load firmware finishes, then the log says Project name: temco_app. |

# 11. Troubleshooting

| What you see | What to do |
| --- | --- |
| Flash tool cannot connect | Hold BOOT, tap RESET, release BOOT. Close PuTTY. Try baud 115200. Check the COM port in Device Manager. |
| Chip type is ESP32, not ESP32-S3 | Choose ESP32-S3 in the tool and flash again. |
| Red FAIL | Check the four addresses. T3_bootloader.bin is at 0x20000. temco_app.bin is not in this step. |
| No text in PuTTY | Speed must be 115200. Do not hold BOOT on a normal reset. |
| No T3_Admin | Wait 30 seconds. The log must say Soft AP is up. If it says temco_app, flash the bootloader again. |
| The phone leaves T3_Admin | It has no internet. Tell the phone to stay on T3_Admin, or use a laptop. |
| The page will not open | You are not on T3_Admin. Use http://192.168.4.1/ , not https. |
| The scan list is empty | The router is 5 GHz only, or the Hub is too far away. Type the 2.4 GHz name by hand. |
| Saved, but WiFi IP stays not connected | The name or password is wrong. Join T3_Admin again and correct it. |
| ping fails | The PC is still on T3_Admin, or it is on a guest network. Join the same Wi-Fi as the address on the page. |
| T3000 scan is empty | ping must work first. Allow T3000 on private networks and scan again. |
| Load firmware does not move | Select the IP from the page. The file must be temco_app.bin. |

# 12. Record sheet

| Item | What you saw |
| --- | --- |
| COM port |  |
| Flash result |  |
| Wi-Fi name you saved |  |
| WiFi IP on the page |  |
| Modbus ID on the page |  |
| ping |  |
| T3000 found it |  |
| Application load |  |

When this sheet is filled, use Guide 2 for MQTT, SNMP, and WireGuard on Wi-Fi. Use Guide 3 when the SIM card is the path.